## Slide 1: K20 to KE5 Conversion
Direct conversion method for specific K20 assemblies

## Slide 2: Direct Conversion Assemblies
Step 1: Gather information about your system.
Model Number VBG-ENX-K20-DMD
Name Gateway1
Assembly I/O: C1/2 A/B Slaves
Size INT
IP Address 192.168.137.15
If certain common Ethernet/IP assemblies were chosen previously the conversion unitality is not needed. Simply delete the old ASi gateway and add the new. Follow these steps.

## Slide 3: Direct Conversion Assemblies
Step 2: Delete the old gateway

## Slide 4: Direct Conversion Assemblies
Step 3: Add the new gateway. Based on your old model number make sure to select the correct one.
VBG-ENX-K20-D  VBG-EP1-KE5-D
VBG-ENX-K20-D-EV24  VBG-EP1-KE5-D
VBG-ENX-K20-DMD  VBG-EP1-KE5-DMD
VBG-ENX-K20-DMD-EV  VBG-EP1-KE5-DMD

## Slide 5: Direct Conversion Assemblies
Step 3: Enter the Name, IP Address, and Size exactly as the old gateway had it. Choose the new assembly based on the below table
Old K20 Assemblies | New KE5 Assemblies
C1 A Slaves | DIO
C1 A Slaves + CI | DIO Diagnostics
C1 A/B Slaves | DIO
C1 A/B Slaves + CI | DIO Diagnostics
C1/2 A/B Slaves | DIO
C1/2 A/B Slaves + CI | DIO Diagnostics
ASI-1+2 Discrete Only | DIO Diagnostics
If your Old K20 assembly is not listed use the conversion utility to properly remap the IO!

## Slide 6: Demonstration

## Slide 7: K20 CI mapping to KE5 Diagnostics
K20 uses CI (Command Interface) for diagnostics data, in which a mailbox mechanism is utilized. For KE5 this process has been simplified by directly mapping the diagnostics data in the input controller tags.
Reference to KE5 direct mapping can be found in manual pg 74. Link Below. https://files.pepperl-fuchs.com/webcat/navi/productInfo/doct/tdoct7070c_eng.pdf?v=20240620103909
Reference to K20 Command interface can be found in the Command Interface manual for the K20. Link Below. https://files.pepperl-fuchs.com/webcat/navi/productInfo/doct/tdoct1484a_eng.pdf?v=20230403152657
If there is any issue with the conversion process, or any question please contact technical support. ask@us.pepperl-fuchs.com

## Slide 8: Pepperl+Fuchs, Inc.
1600 Enterprise Parkway
Twinsburg OH 44087
USA
www.pepperl-fuchs.com
Contact +1 330-486-0001
ask@us.pepperl-fuchs.com
Hours of Operation
8:00 a.m. ET to 6:00 p.m. ET